## Sheet1
A Model of Boiler, Micro-CHP, and DH-CHP, by Gordon Taylor, 1 November 2002
Heating by |  | Boiler | Micro-CHP | Micro-CHP | Micro-CHP | Boiler | Micro-CHP | Fuel Cell | DH-CHP | DH-CHP | DH-CHP | DH-CHP | DH-CHP | DH-CHP
Energy Carrier |  | Nat. Gas | Nat. Gas | Nat. Gas | Nat. Gas | Hydrogen | Hydrogen | Hydrogen | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water
Author |  |  |  |  | Sunpower |  |  |  | Manczyk |  | Frutschi | Haselbacher & Frutschi |  | Frutschi
Reference | [8 empty] | denmark.pdf' |  | ABB Rev. 5/96 | ASME 1997 |  | ABB Rev. 5/96
Plant Name | [8 empty] | Avedore I | Avedore II | ABB GT24 |  |  | ABB GT24
CHP Unit Type | [8 empty] | ST | ST | GTCC | GTCC | Gas Engine | GTCC
Power Cycle
Top Temperature | T1 - C |  |  |  | 550 |  |  |  | 545 | 600 | 1000 |  |  | 1000
Top Temperature | T1 - K |  |  |  | 823 |  |  |  | 818 | 873 | 1273 |  |  | 1273
Bottom Temperature - Cond. | T2 - C | [7 empty] | 10 | 10 | 10 | 2.84 |  | 10
Bottom Temperature - Cond. | T2 - K | [7 empty] | 283 | 283 | 283 |  |  | 283
Carnot Efficiency - Cond. | [8 empty] | 0.65403 | 0.67583 | 0.77769 |  |  | 0.77769
Carnot Factor - Cond. | [10 empty] | 0.78 |  |  | 0.78
Thermal Efficiency - Cond. - NCV | [10 empty] | 0.6066 |  |  | 0.6066
Electricity Generation Efficiency | [10 empty] | 1 |  |  | 1
Electricity Efficiency - Cond - NCV | [8 empty] | 0.45 | 0.482 | 0.6066 | 0.54 | 0.32 | 0.6066
Electricity Output - Cond. | MWe | [7 empty] | 250 | 570 |  | 301.74 | 12.09
Bottom Temperature - BP | T2 - C |  |  |  | 50 |  |  |  | 60 | 60 | 68 | 54 |  | 68
Bottom Temperature - BP | T2 - K |  |  |  | 323 |  |  |  | 333 | 333 | 341 |  |  | 341
Carnot Efficiency - BP | Fraction |  |  |  | 0.60753 |  |  |  | 0.59291 | 0.61856 | 0.73213 |  |  | 0.73213
Carnot Factor - BP | Fraction |  |  |  | 0.5 | [5 empty] | 0.78 |  |  | 0.78
Thermal Efficiency - BP - NCV | Fraction | [9 empty] | 0.57106 |  |  | 0.57106
Electricity Efficiency - BP - NCV | Fraction | [7 empty] | 0.36 | 0.41 | 0.57106 | 0.54 | 0.32 | 0.57106
Electricity Output - BP | MWe | [7 empty] | 215 | 485 |  | 300
Delta Electricity Efficiency - NCV | Fraction | [7 empty] | 0.09 | 0.072 | 0.035538 |  |  | 0.035538
Heat + Electricity Effy. - BP - NCV | Fraction | [7 empty] | 0.92 | 0.95 | 0.86 | 0.86 | 0.86 | 0.86
Heat Efficiency - BP - NCV | Fraction | [7 empty] | 0.56 | 0.54 | 0.28894 | 0.32 | 0.54 | 0.28894
Electricity Efficiency - BP - GCV | Fraction |  | 0.15 | 0.15 | 0.2925 |  | 0.15 | 0.4 | 0.324 | 0.369 | 0.51395 | 0.486 | 0.288 | 0.6
Heat + Electricity Effy. - BP - GCV |  |  | 0.9 | 0.9 | 0.8 |  | 0.85 | 0.85 |  |  | 0.774 |  |  | 0.776
Heat Efficiency - BP - GCV | Fraction |  | 0.75 | 0.75 |  |  | 0.7 | 0.45 | 0.504 | 0.486 | 0.26005 | 0.288 | 0.486 | 0.176
Heat Output | MWth | [11 empty] | 20.4
COP Heating (delta power basis) | Ratio | [7 empty] | 6.2222 | 7.5 | 8.1304 | 9.15 |  | 8.1304
Thermo. heat effy (delta power basis) - NCV | Ratio | [7 empty] | 2.24 | 3.075 | 4.643 | 4.941 | 75336.2832 | 4.643
Thermo. heat effy (delta power basis) - GCV | Ratio | [7 empty] | 2.016 | 2.7675 | 4.1787 | 4.4469 | 67802.6549 | 4.8782
Heat Pump Cycle
Heating Flow Temperature | Tmax - C |  | 70 | 70 | 70 |  | 70 | 70 | 90 | 90 | 90 | 91 |  | 90
| Tmax - K |  | 343 | 343 | 343 |  | 343 | 343 | 363 | 363 | 363 |  |  | 363
Heating Return Temperature | Tmin - C |  | 50 | 50 | 50 |  | 50 | 50 | 60 | 60 | 68 |  |  | 68
| Tmin - K |  | 323 | 323 | 323 |  | 323 | 323 | 333 | 333 | 341 |  |  | 341
Carnot COP Heating | Ratio |  | 17.15 | 17.15 | 17.15 |  | 17.15 | 17.15 | 12.1 | 12.1 | 16.5 |  |  | 16.5
Carnot Factor | Fraction |  | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 |  |  | 0.5
COP Heating (cycle basis) | Ratio |  | 5.7167 | 5.7167 | 5.7167 |  | 5.7167 | 5.7167 | 6.05 | 6.05 | 8.25 |  |  | 8.25
Thermo. heat effy (cycle basis) - NCV | Ratio | [7 empty] | 2.178 | 2.4805 | 4.7112 |  |  | 4.7112
Thermo. heat effy (cycle basis) - GCV | Ratio |  | 0.8575 | 0.8575 | 1.6721 |  | 0.8575 | 2.2867 | 1.9602 | 2.2325 | 4.2401 |  |  | 4.95
Heat to Electricity Power Ratio - 1/alpha | Ratio |  | 5 | 5 | 0 |  | 4.6667 | 1.125 | 1.5556 | 1.3171 | 0.50597 | 0.59259 | 1.6875 | 0.29333
Electricity to Heat Power Ratio - alpha | Ratio |  | 0.2 | 0.2 | #DIV/0! |  | 0.21429 | 0.88889 | 0.64286 | 0.75926 | 1.9764 | 1.6875 | 0.59259 | 3.4091
Boilers Displaced
Domestic Heating by Gas 2001 B | mtoe | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261 | 30.261
Domestic Heating by Gas 2001 B | TWh | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354 | 351.9354
Average Heat Efficiency - GCV | Fraction | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65
Domestic Heat (useful) Net | TWh | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758
Heat Distribution Efficiency | Fraction | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
Domestic Heat Useful Gross | TWh | 228.758 | 228.758 |  |  | 228.758 | 228.758 | 228.758 | 262.9403 | 262.9403 | 262.9403 | 262.9403 | 262.9403 | 262.9403
Heat-Only Boiler
Heat Only Boiler Energy Fraction | Fraction | 1 | 0.1 | 0.1 | 0.33333 | 1 | 0.1 | 0.1 | 0.06 | 0.06 | 0.1 | 0.06 | 0.06 | 0.1
Heat Only Boiler Heat | TWh | 228.758 | 22.8758 |  |  | 228.758 | 22.8758 | 22.8758 | 15.7764 | 15.7764 | 26.294 | 15.7764 | 15.7764 | 26.294
Boiler Efficiency - GCV | Fraction | 0.65 | 0.9 | 0.9 | 0.75 | 0.65 | 0.85 | 0.85 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Gas for Heat Only Boiler | TWh | 351.9354 | 25.4176 |  |  | 351.9354 | 26.9127 | 26.9127 | 19.7205 | 19.7205 | 32.8675 | 19.7205 | 19.7205 | 32.8675
CHP Unit
Cogenerated Heat M | TWh | 0 | 205.8822 | 205.8822 | 152.5054 | 0 | 205.8822 | 205.8822 | 247.1638 | 247.1638 | 236.6462 | 247.1638 | 247.1638 | 236.6462
Gas for Heat & Cogenerated Elec M | TWh | 0 | 274.5096 | #REF! | #REF! | 0 | 294.1175 | 457.5161 | 490.4045 | 508.5676 | 910.0184 | 858.2078 | 508.5676 | 1344.5809
Cogenerated Electricity M | TWh | 0 | 41.1764 | 41.1764 | #DIV/0! | 0 | 44.1176 | 183.0064 | 158.891 | 187.6614 | 467.708 | 417.089 | 146.4675 | 806.7485
Electricity Distribution Efficiency M | Fraction | 0.926 | 1 | 1 | 1 | 0.926 | 1 | 1 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926
Gas for HOB & CHP M | TWh | 351.9354 | 299.9272 | #REF! | #REF! | 351.9354 | 321.0302 | 484.4288 | 510.125 | 528.2881 | 942.8859 | 877.9283 | 528.2881 | 1377.4484
Hydrogen Production Efficiency | Fraction | 1 | 1 | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 |  |  | 1
Gross Gas for HOB & CHP M | TWh | 351.9354 | 299.9272 | #REF! | #REF! | 502.7649 | 458.6145 | 692.0411 | 510.125 | 528.2881 | 942.8859 | #DIV/0! | #DIV/0! | 1377.4484
Electricity Only Plant
Electricity Distribution Efficiency B | Fraction | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926 | 0.926
Matching Electricity B | TWh | 0 | 44.467 | 44.467 | #DIV/0! | 0 | 47.6432 | 197.6311 | 158.891 | 187.6614 | 467.708 | 417.089 | 146.4675 | 806.7485
Gas to Electricity Generation Efficiency B - GCV | Fraction | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463 | 0.5463
Gas for Matching Electricity B | TWh | 0 | 81.3967 | 81.3967 | #DIV/0! | 0 | 87.2107 | 361.763 | 290.8494 | 343.5135 | 856.1376 | 763.4798 | 268.1081 | 1476.75
Savings v Gas
Net Gas for Heat M | TWh | 351.9354 | 218.5305 | #REF! | #REF! | 502.7649 | 371.4038 | 330.2781 | 219.2755 | 184.7746 | 86.7483 | 114.4486 | 260.18 | -99.3016
Gas Saving for Heat B - M | TWh | 0 | 133.4049 | #REF! | #REF! | -150.8295 | -19.4684 | 21.6573 | -158.1896 | -176.3527 | 265.1871 | #DIV/0! | #DIV/0! | 451.237
Specific Carbon Emissions for Gas | gC/kwh gas | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5
Carbon Emissions for Gas Heat & Elec. M | MtC | 19.1805 | 16.346 | #REF! | #REF! | 27.4007 | 24.9945 | 37.7162 | 27.8018 | 28.7917 | 51.3873 | #DIV/0! | #DIV/0! | 75.0709
Carbon Emissions for Gas Heat & Elec. B | MtC | 19.1805 | 23.6166 | 23.6166 | #DIV/0! | 19.1805 | 23.9335 | 38.8966 | 35.0318 | 37.902 | 65.84 | 60.7901 | 33.7924 | 99.6634
Carbon Savings v Gas Heat and Elec B | MtC | 0 | 7.2706 | #REF! | #DIV/0! | -8.2202 | -1.061 | 1.1803 | -8.6213 | -9.6112 | 14.4527 | #DIV/0! | #DIV/0! | 24.5924
Sp. Carbon Savings v Gas Heat and Elec B | gC/kWh th | 0 | 31.7828 | #REF! | #DIV/0! | -35.9341 | -4.6382 | 5.1597 | -37.6876 | -42.0148 | 63.179 |  |  | 107.5041
Savings v Gas & Mix
Specific Carbon Emissions for Mix Elec B | gC/kwh el | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3 | 121.3
Carbon Emissions, Gas Heat & Mix Elec B | MtC | 19.1805 | 24.5743 | #REF! | #REF! | 19.1805 | 24.9596 | 43.1531 | 38.454 | 41.9438 | 75.9135 | 69.7734 | 36.947 | 117.0391
Carbon Savings v Gas Heat & Mix Elec B | MtC | 0 | 8.2283 | #REF! | #REF! | -8.2202 | -0.034889 | 5.4369 | 10.6522 | 13.1521 | 24.5262 | #DIV/0! | #DIV/0! | 41.9681
Sp. Carbon Savings v Gas Heat & Mix Elec B | gC/kWh th | 0 | 35.9694 | #REF! | #REF! | -35.9341 | -0.15251 | 23.767 | 46.5652 | 57.4936 | 107.2145 |  |  | 183.4608
|  | Micro-CHP | Micro-CHP |  |  |  |  | Fuel Cell |  |  |  | v Gas Elec. | v Mix Elec. | CHP-GTCC | CHP-GTCC
| Elec Effy | C Svg. Gas | C Svg. Mix |  |  |  |  | C Svg. Gas |  |  |  | C Saving | C Saving | C Svg. Gas | C Svg. Mix
| Fraction | gC/kWh ht | gC/kWh ht |  |  |  |  | MtC/y |  |  |  | gC/kWh heat | gC/kWh heat | gC/kWh ht | gC/kWh ht
| 0.1 | 28.6 | 31.21 | [8 empty] | 0 | #REF! | 7.88 | 11.18
| 0.2 | 35.42 | 41.4 | [8 empty] | 0 | #REF! | 13.97 | 21.71
| 0.3 | 44.52 | 54.99 |  |  |  |  | -5.66 |  |  |  | 0 | #REF! | 22.62 | 36.66
| 0.4 | 57.26 | 74.01 |  |  |  |  | -1.72 |  |  |  | 0 | #REF! | 35.86 | 59.56
| 0.5 | 76.37 | 102.53 | [8 empty] | 0 | #REF! | 58.7 | 99.07
| 0.6 | 108.21 | 150.08 | [8 empty] | 0 | #REF! | 107.5 | 183.46
|  | Current | Current |  |  |  |  | Best |  |  |  | Current | Current | Current | Current
| 0.15 | 31.78 | 35.97
6.205
| 0.515 | [10 empty] | 0 | #REF! | 63.63 | 107.63
Table 2 Carbon Savings for Various Options Supplying Useful Heat of 229 TWh/y
v Gas Boilers at 0.65, and Gas or Mix Electricity
Heating by |  | Boiler | Micro-CHP | Micro-CHP | Micro-CHP | Boiler | Micro-CHP | Fuel Cell | DH-CHP | DH-CHP | DH-CHP | DH-CHP | DH-CHP | DH-CHP
Energy Carrier |  | Nat. Gas | Nat. Gas | Nat. Gas | Nat. Gas | Hydrogen | Hydrogen | Hydrogen | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water | Hot Water
Domestic Heat (useful) Net | TWh/y | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | 228.758 | #VALUE! | #VALUE! | 228.758
Carbon Emissions for Gas Boilers | MtC/y | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805 | 19.1805
Carbon Savings v Gas Heat and Electricity | MtC/y | 0 | 7.2706 | #REF! | #DIV/0! | -8.2202 | -1.061 | 1.1803 | -8.6213 | -9.6112 | 14.4527 | #REF! | #REF! | 24.5924
Carbon Savings v Gas Heat and Electricity | % | 0 | 37.9061 | #REF! | #DIV/0! | -42.8571 | -5.5318 | 6.1538 | -44.9485 | -50.1094 | 75.3511 | #REF! | #REF! | 128.2159
Specific Carbon Savings v Gas Heat and Electricity | gC/kWh th | 0 | 31.7828 | #REF! | #DIV/0! | -35.9341 | -4.6382 | 5.1597 | -37.6876 | -42.0148 | 63.179 |  |  | 107.5041
Carbon Savings v Gas Heat & Mix Electricity | MtC/y | 0 | 8.2283 | #REF! | #REF! | -8.2202 | -0.034889 | 5.4369 | 10.6522 | 13.1521 | 24.5262 | #REF! | #REF! | 41.9681
Carbon Savings v Gas Heat & Mix Electricity | % | 0 | 42.8993 | #REF! | #REF! | -42.8571 | -0.1819 | 28.346 | 55.5364 | 68.5703 | 127.8705 | #REF! | #REF! | 218.8065
Specific Carbon Savings v Gas Heat & Mix Electricity | gC/kWh th | 0 | 35.9694 | #REF! | #REF! | -35.9341 | -0.15251 | 23.767 | 46.5652 | 57.4936 | 107.2145 |  |  | 183.4608
Note on M8: Gordon Taylor: Based on an annual energy calculation
Note on N8: Gordon Taylor: Based on an annual energy calculation
Note on M57: Gordon Taylor: The value of 0.06 comes from the paper by Haselbacher & Frutschi